On-line UPS 1k-10kVA (220V)

| Model | MR-US1K | MR-US2K | MR-US3K | MR-US6K | MR-US10K |
| --- | --- | --- | --- | --- | --- |
| Rated Capacity | 1kVA / 1kW | 2kVA / 2kW | 3kVA / 3kW | 6kVA / 6kW | 10kVA / 10kW |
| Output |  |  |  |  |  |
| Output Voltage | 208 / 220 / 230 / 240VAC |  |  |  |  |
| Output Frequency | 50 / 60Hz ± 0.1 % |  |  |  |  |
| Output Harmonic Distortion | ≤3% THD(linear load), ≤5% THD(non-linear load) |  |  |  |  |
| Output Power Factor | 1.0 |  |  |  |  |
| Switching Time | AC Mode to Battery Mode 0ms, Inverter to Bypass 4ms(Typical) |  |  |  |  |
| UPS Type | Double-conversion On-Line |  |  |  |  |
| Waveform Type | Pure Sine wave |  |  |  |  |
| Input |  |  |  |  |  |
| Rated Input Voltage | 208 / 220 / 230 / 240VAC |  |  |  |  |
| Input Voltage Range | 110 – 300VAC, 110 – 176VAC, 280 – 300VAC (power limited) |  |  |  |  |
| Input Frequency | 50 / 60 ± 6Hz (Default), ±10Hz (Adjustable) |  |  |  |  |
| Input Power Factor | ≥0.99 |  |  |  |  |
| Load Efficiency |  |  |  |  |  |
| AC Mode | Full load 94.5%@220VAC | Full load 95.5%@220VAC | Full load 95.5%@220VAC | Full load effciency 95%, Maximum efficiency 95.5% |  |
| Battery Mode | Full load 89.5%@36VDC | Full load 91.5%@72VDC | Full load 91.5%@96VDC | Full load effciency 94.8% (20pcs batteries), Maximum efficiency 95.3% |  |

BATTERY 220V

| Battery |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Battery Type | Lead-acid battery |  |  |  |  |
| Battery Quantity | 12V / 7Ah * 2 | 12V / 7Ah * 4 | 12V / 7Ah * 6 | 12V / 7Ah (9Ah optional)*16 |  |
| Typical Recharge Time | 4 – 5 hours recover to 90% capacity |  |  | 7 – 9 hours recover to 90% capacity |  |
| Physical |  |  |  |  |  |
| Form Factor | Tower |  |  |  |  |
| Dimension,D*W*H(mm) | 276 * 145 * 225 | 392 * 145 * 225 | 395 * 190 * 325 | 460 * 190 * 615 |  |
| Net Weight(kg) | 8.6 | 14.3 | 20.5 | 50.6 | 50.8 |
| Communication Interface | RS232, USB, EPO |  |  | RS232, USB, EPO, SNMP, Dry-contact, Maintenance Connector |  |
| Communications & Management |  |  |  |  |  |
| Control Panel | Multifunction LCD status and control console |  |  |  |  |
| Alarm | Alarm every 8 seconds in battery mode |  |  |  |  |
|  | Alarm for low battery every second |  |  |  |  |
|  | Alarm on overload every second |  |  |  |  |
| Protection | Short circuit, Overload , Overcharge and Overdischarge protection |  |  |  |  |
| Environment |  |  |  |  |  |
| Operating Temperature | 0°C – 40°C |  |  |  |  |
| Storage Temperature | -15°C – 60°C (Battery: 0°C – 40°C) |  |  |  |  |
| Relative Humidity | 20 – 95% (non-condensing) |  |  |  |  |
| Audible Noise | Less than 50dB (1 meter from surface) |  |  |  |  |
| Standard & Approvals |  |  |  |  |  |
| Safety | IEC / EN62040-1, IEC / EN60950-1 |  |  |  |  |
| EMC | IEC/EN62040-2, IEC61000-4-2, IEC61000-4-3, IEC61000-4-4, IEC61000-4-5, IEC61000-4-6, IEC61000-4-8 |  |  |  |  |